# Ad 9.2 Zestawienie agregatów wody lodowej

|  | (A) | (B) | (C) | (D) |
| --- | --- | --- | --- | --- |
| Model reference | EWAQ240DAYN | EWAQ130DAYN | EWAQ150DAYN | EWAQ150DAYN |
| Application option | Std | Std | Std | Std |
| Option codes | BDDQ- | BDDQ- | BDDQ- | BDDQ- |
| Cooling |  |  |  |  |
| Required total capacity | 224,8kW | 114,8kW | 153,1kW | 153,1kW |
| Deviation | 2,3% | 14,1% | -0,3% | -0,3% |
| Capacity | 230,0kW | 131,0kW | 152,6kW | 152,6kW |
| Power input | 77,1kW | 43,7kW | 52,8kW | 52,8kW |
| EER | 3,0 | 3,0 | 2,9 | 2,9 |
| ESEER | 0 | 0 | 0 | 0 |
| Sound data |  |  |  |  |
| Sound power | 91,0dBA | 88,0dBA | 89,0dBA | 89,0dBA |
| Sound pressure level @ 1m | 71,0dBA | 69,2dBA | 70,2dBA | 70,2dBA |
| Sound pressure level @ 5m | 63,4dBA | 60,9dBA | 61,9dBA | 61,9dBA |
| Sound pressure level @ 10m | 58,7dBA | 56,0dBA | 57,0dBA | 57,0dBA |
| Eurovent certified | Yes | Yes | Yes | Yes |

## 9.2.1. Szczegóły agregatu A

|  | Model reference | Application option | Option codes |
| --- | --- | --- | --- |
| General data | EWAQ240DAYN | Std | BDDQ- |

|  | Condenser | Family | Refrigerant |
| --- | --- | --- | --- |
| Selection data | Air cooled | Cooling only | R410A |

|  | Type | Quantity | Number of capacity steps |
| --- | --- | --- | --- |
| Compressor | Scroll | 2 | 22/28-40/50/56-72/78-100 |

|  | Required total capacity | Deviation | Capacity | Power input | EER |
| --- | --- | --- | --- | --- | --- |
| Cooling | 224,8kW | 2,3% | 230,0kW | 77,1kW | 3,0 |

| Evaporator | Leaving fluid T | Entering fluid T | Delta T | Fluid type | % Weight | Fluid flow rate | Fluid pressure drop |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Cooling | 7,0°C | 12,0°C | 5,0°C | Ethylene | 30% | 12,4l/s | 126459Pa |

|  | Type | Ambient summer temperature |
| --- | --- | --- |
| Condenser | Air cooled | 32,0°C |

|  | Power supply | Max. start current | Max. run current | Max. compressor run current | Fuses | Voltage limits |
| --- | --- | --- | --- | --- | --- | --- |
| Electrical data | 3x400V, 50Hz (YN) | 426,0A | 262,0A | 65,0A | 3 | +/-10% |

|  | Height | Width | Depth | Weight |
| --- | --- | --- | --- | --- |
| Mechanical data | 2311mm | 2000mm | 4850mm | 3150,0kg |

|  | 63Hz | 125Hz | 250Hz | 500Hz | 1000Hz | 2000Hz | 4000Hz | 8000Hz |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sound spectrum | 66Hz | 71Hz | 75Hz | 88Hz | 84Hz | 84Hz | 76Hz | 57Hz |

|  | Sound power | Sound pressure level @ 1m | Sound pressure level @ 5m | Sound pressure level @ 10m |
| --- | --- | --- | --- | --- |
| Sound data | 91,0dBA | 71,0dBA | 63,4dBA | 58,7dBA |

Sound power data is in accordance with ISO3744. Measurement is at nominal condition. Sound pressure is calculated for indication purposes. Calculation is only valid for free field conditions: Lp=Lw-10Log(S).

| Option data |  |
| --- | --- |
| Standard options | Main switch |
| Selected options | Suction stop valve, Gateway for LON, Low noise, Inverter fan Single pump, Buffer tank |

## 9.2.2. Szczegóły agregatu B

|  | Model reference | Application option | Option codes |
| --- | --- | --- | --- |
| General data | EWAQ130DAYN | Std | BDDQ- |

|  | Condenser | Family | Refrigerant |
| --- | --- | --- | --- |
| Selection data | Air cooled | Cooling only | R410A |

|  | Type | Quantity | Number of capacity steps |
| --- | --- | --- | --- |
| Compressor | Scroll | 4 | 0-25-50-75-100 |

|  | Required total capacity | Deviation | Capacity | Power input | EER |
| --- | --- | --- | --- | --- | --- |
| Cooling | 114,8kW | 14,1% | 131,0kW | 43,7kW | 3,0 |

| Evaporator | Leaving fluid T | Entering fluid T | Delta T | Fluid type | % Weight | Fluid flow rate | Fluid pressure drop |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Cooling | 7,0°C | 12,0°C | 5,0°C | Ethylene | 30% | 7,1l/s | 101664Pa |

|  | Type | Ambient summer temperature |
| --- | --- | --- |
| Condenser | Air cooled | 32,0°C |

|  | Power supply | Max. start current | Max. run current | Max. compressor run current | Fuses | Voltage limits |
| --- | --- | --- | --- | --- | --- | --- |
| Electrical data | 3x400V, 50Hz (YN) | 269,0A | 160,0A | 35,0A | 3 | +/-10% |

|  | Height | Width | Depth | Weight |
| --- | --- | --- | --- | --- |
| Mechanical data | 2311mm | 2000mm | 2631mm | 1500,0kg |

|  | 63Hz | 125Hz | 250Hz | 500Hz | 1000Hz | 2000Hz | 4000Hz | 8000Hz |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sound spectrum | 64Hz | 70Hz | 73Hz | 81Hz | 85Hz | 80Hz | 72Hz | 61Hz |

|  | Sound power | Sound pressure level @ 1m | Sound pressure level @ 5m | Sound pressure level @ 10m |
| --- | --- | --- | --- | --- |
| Sound data | 88,0dBA | 69,2dBA | 60,9dBA | 56,0dBA |

Sound power data is in accordance with ISO3744. Measurement is at nominal condition. Sound pressure is calculated for indication purposes. Calculation is only valid for free field conditions: Lp=Lw-10Log(S).

| Option data |  |
| --- | --- |
| Standard options | Main switch |
| Selected options | Gateway for LON, Suction stop valve, Single pump, Inverter fan Low noise, Buffer tank |

## 9.2.3. Szczegóły agregatów C i D

|  | Model reference | Application option | Option codes |
| --- | --- | --- | --- |
| General data | EWAQ150DAYN | Std | BDDQ- |

|  | Condenser | Family | Refrigerant |
| --- | --- | --- | --- |
| Selection data | Air cooled | Cooling only | R410A |

|  | Type | Quantity | Number of capacity steps |
| --- | --- | --- | --- |
| Compressor | Scroll | 4 | 0-25-50-75-100 |

|  | Required total capacity | Deviation | Capacity | Power input | EER |
| --- | --- | --- | --- | --- | --- |
| Cooling | 153,1kW | -0,3% | 152,6kW | 52,8kW | 2,9 |

| Evaporator | Leaving fluid T | Entering fluid T | Delta T | Fluid type | % Weight | Fluid flow rate | Fluid pressure drop |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Cooling | 7,0°C | 12,0°C | 5,0°C | Ethylene | 30% | 8,2l/s | 101689Pa |

|  | Type | Ambient summer temperature |
| --- | --- | --- |
| Condenser | Air cooled | 32,0°C |

|  | Power supply | Max. start current | Max. run current | Max. compressor run current | Fuses | Voltage limits |
| --- | --- | --- | --- | --- | --- | --- |
| Electrical data | 3x400V, 50Hz (YN) | 320,0A | 177,0A | 39,0A | 3 | +/-10% |

|  | Height | Width | Depth | Weight |
| --- | --- | --- | --- | --- |
| Mechanical data | 2311mm | 2000mm | 2631mm | 1550,0kg |

|  | 63Hz | 125Hz | 250Hz | 500Hz | 1000Hz | 2000Hz | 4000Hz | 8000Hz |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sound spectrum | 65Hz | 74Hz | 75Hz | 85Hz | 84Hz | 80Hz | 74Hz | 65Hz |

|  | Sound power | Sound pressure level @ 1m | Sound pressure level @ 5m | Sound pressure level @ 10m |
| --- | --- | --- | --- | --- |
| Sound data | 89,0dBA | 70,2dBA | 61,9dBA | 57,0dBA |

Sound power data is in accordance with ISO3744. Measurement is at nominal condition. Sound pressure is calculated for indication purposes. Calculation is only valid for free field conditions: Lp=Lw-10Log(S).

| Option data |  |
| --- | --- |
| Standard options | Main switch |
| Selected options | Gateway for LON, Inverter fan, Suction stop valve, Low noise Buffer tank, Single pump |